## TUNING THE TIME TO DETECT DISCONNECTION IN TCP/IP

This article is for use with:

- Multi-station PcVue (Full TCP/IP or NetBIOS over TCP/IP).

- Ethernet protocols such as Open Modbus TCP/IP.

Solution

You can adjust this by modifying Windows Registry.

|  | Back up the Registry first, e.g. by using its File.Export facility. |
| --- | --- |

All of the TCP/IP parameters are Registry values under the following key:

HKEY_LOCAL_MACHINE

\SYSTEM

\CurrentControlSet

\Services

\Tcpip

\Parameters

Parameter

The parameter to add is TcpMaxDataRetransmissions.

Setting

Default value of 5 is too high for a 100 Mbit network.

- With a value of 2, the time to detect disconnection is reduced (around 3 times better)