WebVue Redundancy for PcVue 12

Description: This document describes on how to setup and test behaviors of NLB for WebVue Redundancy

Keywords: PcVue, WebVue, Redundancy

ARC Informatique - Head Office address: 2 Avenue de la Cristallerie 92310 SEVRES - FRANCE

Private Limited Company capitalised at 750 000 € - RCS Nanterre B 320 695 356- APE 722 C - SIREN 320 695 356- VAT N° FR 19 320 695 356

Last Revision Date: 26-Dec-19

# Authorization

|  | Name | Stamp | Date |
| --- | --- | --- | --- |
| Written by | Kantha Rao Simanjalam |  | 1 Aug 2018 |
| Checked by | Nicolas Kunzer |  | 7 Aug 2018 |
| Authorized by |  |  |  |

# Revision history

| Revision | Author | Action | Editing | Date | Distribution |
| --- | --- | --- | --- | --- | --- |
| 12.0a | KASI | Write |  | 27/07/2018 |  |
|  | NK | Document Review |  | 03/08/2018 |  |
| 12.0b | KASI | Amendment |  | 06/08/2018 |  |

The information in this book is subject to change without notice and does not represent a commitment on the part of the publisher.  The software described in this book is furnished under a license agreement and may only be used or copied in accordance with the terms of that agreement.  It is against the law to copy software on any media except as specifically allowed in the license agreement.  No part of this manual may be reproduced or transmitted in any form or by any means without the express permission of the publisher.  The author and publisher make no representation or warranties of any kind with regard to the completeness or accuracy of the contents herein and accept no liability of any kind including but not limited to performance, merchantability, fitness for any particular purpose, or any losses or damages of any kind caused or alleged to be caused directly or indirectly from this book. In particular, the information contained in this book does not substitute to the instructions from the products’ vendor.

All product names and trademarks mentioned in this document belong to their respective owner

# SUMMARY

1 Introduction	5

Objective	5

2 Overview	6

3 Platform implemented	7

4 Document description	8

5 NLB Setup	9

Prerequisites	9

Setting Up Virtual IP and Redirection	9

NLB Setup	16

NLB Verification	21

6 WebVue Setup Using Web Deployment Console	23

WebVue Setup	23

7 Observed Behavior	27

Preparation	27

When Server Status is Changing	29

When NLB Server Status is Changing	31

When IIS Status is Changing	33

When PcVue Status is Changing	34

Summary	36

Other Possible Solutions	36

# Introduction

## Objective

This document has several objectives:

#### Study how to implement a redundancy for PcVue acting as a Web backend.

#### Give a guide for the Support Team (hence our customers) where all steps of the solution implementation are described.

# Overview

The selected solution is the Microsoft Network Load Balancing feature (NLB). NLB is a feature that distributes network traffic among multiple servers or virtual machines within a Cluster to avoid overloading any one host and improve performance. The cluster is identified by an IP named Virtual IP. More information on NLB can be found here.

Figure 1 : Architecture Overview

# Platform implemented

Tests have been done using the following platform

- A Domain Controller Server

- 2 Servers to be used as WebVue Server. These servers need to be domain joined to Domain Controller Server.

Table 1: Environment

| Item | Description |
| --- | --- |
| OS for all stations | Windows Server 2016 |
| Domain Name | AVENGERS.LOCAL |
| PcVue | 12.0.0.24488 |

Table 2: Stations network configuration

|  | IP | Machine Name | FQDN |
| --- | --- | --- | --- |
| Domain Server | 10.100.5.40 | LAB-SERVER | LAB.AVENGERS.LOCAL |
| SERVER 1 | 10.100.5.66 | SERVER1-ANTMAN | SERVER1-ANTMAN.AVENGERS.LOCAL |
| SERVER 2 | 10.100.5.65 | SERVER2-THEWASP | SERVER2-THEWASP.AVENGERS.LOCAL |
| NLB Cluster | 10.100.5.100 | ---- | www.lab.com |

# Document description

The first part of this document describes how to setup pre-requisite for NLB, NLB and how to verify NLB setup.

The second part describes how to setup WebVue using Web Deployment Console (WDC).

The third part describes the first layer developed: our tabular archive format. This chapter introduces configuration concept, table format, traces, limitations…

# NLB Setup

## Prerequisites

Before start with NLB setup, we need to have below items ready:

      - A URL with redirection to a virtual IP. This can be done using DNS Manager in DNS Server and will be shown in section 2.1.1.

      - 2 Servers with static IP to be load balanced. Network Load Balancing feature will be enabled and setup on these servers, as per section 2.1.2

      - You also will need to have license for each PcVue server to be able to use WebVue feature.

### Setting Up Virtual IP and Redirection

Login to Domain Controller Server, and open DNS Manager.

            - Right Click on Forward Lookup Zones and select New Zone. Click Next.

Figure 2

            - Leave default setting (primary zone) for Zone Type

Figure 3

            - Replication Zone leave it at “To all DNS servers in this domain”

Figure 4

            - Enter zone name and click next. In this example, it is lab.com

            - For Dynamic Update, select Allow both nonsecure and secure dynamic updates. Click Next and Finish.

Figure 5

            - Right click on Reverse Lookup Zones, Click New Zone and click next

            - Select Primary zone, and keep the checkbox at bottom ticked for Zone Type

Figure 6

            - For replication scope, choose “To all DNS servers in this domain”

Figure 7

            - Stick with IPv4 Reverse Lookup Zone

Figure 8

            - Key in the first 3 ip address of DNS server as below.

Figure 9

Figure 10

            - If hit error as below, you may ignore, this is fine because it means the reverse lookup zone is already exist and you may proceed with next step.

Figure 11

            - Now go to Forward Lookup Zone, right click on lab.com and choose New Host (A or AAAA)…

Figure 12

            - Enter name and the virtual IP. Click Add Host and Done

Figure 13

            - Go back to Reverse Lookup Zone and refresh, the virtual IP pointer would have been created there as well.

            - To verify, you may open command prompt and nslookup www.lab.com. Results should be as below:

Figure 14

## NLB Setup

Below steps is to setup Network Load Balancing (NLB)

- Right Click on Network Load Balancing Clusters and Choose New Cluster. Key in FQDN for the second server and Click Connect. Once get interface name, click Next.

Figure 15

- Set Priority 2 and click Next.

Figure 16

- Key in virtual IP address and Click Next.

Figure 17

- Key in FQDN for virtual IP, select multicast and click next

Figure 18

- Remove existing port rules and add new rule for port 80 and 443 each. Then click Finish

Figure 19

Figure 20

- Repeat the same to add another host for Server1.

Figure 21

- Make sure to set priority 1 for server 1, or any other priority based on your preference. Click Next, then Finish.

Figure 22

- After done, you should see list of 2 server as below, with status Converged. Go to server 2, open Network Load Balancing and you should see the same setup has been replicated.

Figure 23

- Open command prompt in both servers and perform ipconfig. Now you will see additional 1 IPV4 address, with the virtual IP.

Figure 24

Setup for both server 1 and server 2 above were done with the same domain logon user. If the logon user for both server 1 and server 2 are different, then you need to do the following before both servers appear converged.

Go to Options -> Credentials -> Provide credential to the other server. For example, if you are in server 1, provide credential for server 2, and vice versa.

## NLB Verification

Before make verification, it is recommended to do following changes in both server 1 and server 2. This is recommended to

- Launch Notepad as Administrator

- Navigate and open file C:\inetpub\wwwroot\iisstart.htm

- Add below code line right below </head> in the htm file and save

<h1>Hostname is :SERVER1</h1>

- In server 2, do the same changes, but with text name amended to SERVER2

With the amended of iisstart file, we will be able to see which server is serving when we access website using virtual IP/URLs.

- Figure 25

To verify:

- Open Chrome Browser

- Type https://www.lab.com and browse

- You should be able to see IISStart page with text “Hostname is: SERVER1”

- Launch Network Load Balancing Manager from either Server 1 or Server 2.

- Right Click on Server 1 -> Control Host -> Stop

- Go to browser again, and refresh.

- You should be able to see IISStart page with text “Hostname is: SERVER2”

- Launch Network Load Balancing Manager from either Server 1 or Server 2.

- Right Click on Server 1 -> Control Host -> Start

- Go to browser again, and refresh.

- Now text in browser should change again to “Hostname is: SERVER1”

- This is because priority for Server1 is higher than Server2.

# WebVue Setup Using Web Deployment Console

## WebVue Setup

We use PcVue Web Deployment Console (WDC) to setup web configuration and to bind virtual IP to our WebVue.

- Launch WDC and click Deploy New Server. Give an appropriate Alias and click Next. Click Yes to continue with Site Deployment. Then Click Quick Setup.

Figure 26

- Give Website name and click Next.

Figure 27

- Key in the virtual IP FQDN to bind with hostname. In this example is www.lab.com. Click Next.

Figure 28

- If there is already a certificate, choose the certificate to be imported. For testing, choose option to create self-sign certificate. For self-sign, enter virtual IP FQDN to create certificate. Then Click Next.

Figure 29

Figure 30

- Click + sign to add new backend. Enter Server1’s FQDN as the host for backend configuration. Click Next.

Figure 31

- Select WebVue role for installation and click deploy.

Figure 32

- Once deploy complete, click Clients and make sure WebVue is deployed. If WebVue is not appear, you can click Roles & Service, make sure WebVue is ticked, and deploy again before verifying.

- You may click on WebVue to see more details on setup. You can also click Configure under Registry Service to verify that all the service are bound to www.lab.com.

# Observed Behavior

This chapter describes the PcVue Project that need to be prepared, and the list of test scenarios performed and the observed behavior. Tests are separated by several category below.

- Please take note that Server 1 is on priority 1, and Server 2 is on priority 2. If you did the setup with different priority, results might differ.

## Preparation

- Create a new project in Server 1.

- Open Mimic and create a text object “Server 1”

Figure 33

- Open Application Explorer -> Communication -> Servers -> Web & Mobile Back ends -> Create new -> Select Mimic and Press OK

Figure 34

- Create 2 users, a and b, and assign to DEFPROFILE.

- Now do the same in Server 2, but make sure the text is now saying Server 2 (Step 2)

## When Server Status is Changing

For this scenario, we will test behavior when 1 of the servers is in shutdown or suspend status. You can do these actions using the NLB console. For these cases:

- Both host status in NLB Manager is Started, IIS is running, and PcVue application is running with license dongle attached on both servers.

- Browser used is located outside from Server1 and Server2.

S1 = Server 1, S2 = Server 2

Green = Running, Red = Stopped

| Test sequence | S1 | S2 | Result | Comment |
| --- | --- | --- | --- | --- |
| Start S1 and S2, and start PcVue |  |  |  |  |
| Login WebVue |  |  | Session created on Server 1 |  |
| Power Off S2 |  |  | No effect |  |
| Start S2 and PcVue |  |  | No effect |  |
| Logout WebVue |  |  | Session removed on Server 1 |  |
| Login to WebVue |  |  | Session will connect to Server 1 |  |
| Logout WebVue |  |  | Session removed on Server 1 |  |
| Clear Browser Cache, and login again |  |  | Session will now reconnect to S2. | This situation is not normal as Server 1 is in priority 1. |
| Power Off S1 |  |  | No effect |  |
| Start S1 and PcVue |  |  | No effect |  |
| Logout WebVue |  |  | Session removed on Server 2 |  |
| Clear browser cache |  |  | No effect |  |
| Login WebVue |  |  | Session created on Server 1 |  |
| Power Off S1 |  |  | Client loses connection “Your session has been logged out”. |  |
| Refresh browser |  |  | Browser will go back to login page |  |
| Login WebVue |  |  | Session created on Server 2 |  |
| Power Off S2 |  |  | Client loses connection “Your session has been logged out”. |  |
| Refresh browser |  |  | “This site can’t be reached” error message |  |

- Redundancy happen correctly when server is down or not reachable.

- When server 2 is recently powered on, it will swing to be the active server

## When NLB Server Status is Changing

For this scenario, we will test behavior by changing host status inside NLB Cluster. Status available is Start, Stop, and Suspend. For these tests:

- PcVue and IIS is always running

- Browser used is located outside from Server1 and Server2.

S1 = Server 1, S2 = Server 2

Green = NLB Started, Red = NLB Stopped, Yellow = NLB Suspended

| Test sequence | S1 | S2 | Result | Comment |
| --- | --- | --- | --- | --- |
| Start S1 and S2, and start PcVue |  |  |  |  |
| Login WebVue |  |  | Session created on Server 1 |  |
| Stop S2 in NLB |  |  | No effect |  |
| Start S2 in NLB |  |  | No effect |  |
| Logout WebVue |  |  | Session removed on Server 1 |  |
| Stop S1 in NLB |  |  | No effect |  |
| Login WebVue |  |  | Session created on Server 2 |  |
| Logout WebVue |  |  | Session removed on Server 2 |  |
| Start S1 in NLB |  |  | No effect |  |
| Login WebVue |  |  | Session will be created in Server 2. | This point is not normal as Server 1 is in priority 1. |
| Logout WebVue, clear browser cache, and login WebVue again |  |  | Session created on Server 1 | Clearing the cache solved this issue. |
| Stop S1 in NLB |  |  | Client loses connection when browser is refreshed, or after waiting several seconds |  |
| Login WebVue |  |  | Session created on Server 2 |  |
| Stop S2 in NLB |  |  | Client loses connection when browser is refreshed, or after waiting several seconds |  |
| Refresh browser |  |  | “This site can’t be reached” error message. |  |
| Start S1 and S2 in NLB |  |  | No effect |  |
| Refresh Browser and Login WebVue |  |  | Session created on Server 1 |  |
| Suspend S1 in NLB |  |  | Client loses connection when browser is refreshed, or after waiting several seconds |  |
| Refresh browser and Login WebVue |  |  | Session created on Server 2 |  |
| Resume S1, Start S1 and suspend S2 in NLB |  |  | Client loses connection when browser is refreshed, or after waiting several seconds |  |
| Refresh browser and Login WebVue |  |  | Session created on Server 1 |  |
| Suspend S1 in NLB |  |  | Client loses connection, or after waiting several seconds |  |
| Refresh browser |  |  | “This site can’t be reached” error message. |  |
| Resume S1 and S2, Start S1 and S2, by sequence |  |  | No Effect |  |

- For NLB host status manipulation, when the host is stopped or suspended, it will route traffic to another server.

- If both servers are stopped or suspended, then it will show site can’t be reached.

- Sometimes, page need to be reloaded, or wait several seconds to reflect correct serving server. This is because of previous loaded website is still in cache.

## When IIS Status is Changing

We will test this scenario by changing status of IIS to either Stop or Start. For these tests:

- PcVue and Server will be in running state for this test case. NLB Host status is running for both

- Browser used is located outside from Server1 and Server2.

- IIS Status here is referring to status of both default website and PcVue website.

S1 = Server 1, S2 = Server 2

Green = IIS Running, Red = IIS Stopped

| Test sequence | S1 | S2 | Result | Comment |
| --- | --- | --- | --- | --- |
| Login WebVue |  |  | Session created on Server 1 |  |
| Stop IIS on S2 |  |  | No effect |  |
| Start IIS on S2 |  |  | No effect |  |
| Logout WebVue |  |  | Session removed on Server 1 |  |
| Stop IIS on S1 |  |  | No effect |  |
| Login WebVue |  |  | “This site can’t be reached” error message. |  |
| Start IIS on S1 |  |  |  |  |
| Refresh Browser and Login WebVue |  |  | Session created on Server 1 |  |
| Stop IIS on S1 |  |  | Client loses connection |  |
| Start IIS on S1 |  |  | Refresh browser and session on Server 1 resumed (no need to relogin) |  |

- NLB does not seems to route traffic when IIS service is down.

## When PcVue Status is Changing

This scenario will be tested by running or stopping PcVue

S1 = Server 1, S2 = Server 2

Green = PcVue Running, Red = PcVue Stopped

| Test sequence | S1 | S2 | Result | Comment |
| --- | --- | --- | --- | --- |
| Clear browser cache |  |  | No effect | Done to reset all. |
| Login WebVue |  |  | Session created on Server 1 |  |
| Stop PcVue on S2 |  |  | No effect |  |
| Start PcVue on S2 |  |  | No effect |  |
| Logout WebVue |  |  | Session removed on Server 1 |  |
| Stop PcVue on S1 |  |  | No effect |  |
| Login WebVue |  |  | “The supervisor software is not accessible” Error Message |  |
| Start PcVue on S1 |  |  | No Effect |  |
| Click back on browser and Login WebVue |  |  | Session created on Server 1 |  |
| Stop PcVue on S1 |  |  | Client loses connection |  |
| Start PcVue on S1 |  |  | No effect |  |
| Refresh browser |  |  | Session on server 1 resumed (no need to login again) |  |

- NLB is not routing the traffic when PcVue service is down.

## Summary

Network Load Balancing works as expected under below scenarios:

- Server is down or not accessible

- Host is manually stopped or suspended in Network Load Balancing.

In both cases, NLB will route traffic to next available server based on priority.

In both cases, the WebVue session is lost.

NLB have a limitation that it is not able to detect when IIS is down, or PcVue is not running.

## Other Possible Solutions

For cases where IIS is down, there is a possibility of doing a workaround by creating a script to verify IIS status, and send command to NLB to stop or start the host. This answer was provided here, and follow up link is here.

Another possibility is by using third party software that can check status of the website or checks for error on page to do routing. This kind of solution might require further training and might incur cost to implement.